  - DELAYED EGRESS LOCKS

    - Delayed Egress Locks, Integrated:

      - Operation: When unauthorized egress is initiated, delayed egress lock delays egress through the door for 15 or 30 seconds. Meanwhile, the person exiting must wait while personnel or security respond. The door unlocks after 15 seconds have elapsed, permitting egress. A signal from the fire life safety system will release the lock for uninhibited egress in an emergency. 30 second delay available where approved.

** NOTE TO SPECIFIER **   Delete model not required.

      - Product: Model 1511S - Single Exit Check Integrated Delayed Egress Lock as manufactured by SDC Security Door Controls.

      - Product: Model 1511T - Tandem Exit Check Integrated Delayed Egress Lock as manufactured by SDC Security Door Controls.

        - 1511S - 1650 lb (748 Kg) of holding force, dual coil 830/450 mA at 12/24 VDC operation.

        - 1511T -  (2X) 1650 lb (748 Kg) holding force, dual coil 1500/850 mA at 12/24 VDC operation.

        - Activated by door movement or sense bar  unlock delay and nuisance delay per code specification.

        - Emergency release input, Mode status outputs, Digital countdown display, Selectable voice or tone warning.

      - Product: Model 1511SE - Energy Saver Single Exit Check Integrated Delayed Egress Lock as manufactured by SDC Security Door Controls.

        - 1200 lb (544 kg) holding force, dual coil, 400/275 mA at 12/24VDC operation

      - Product: Model 1511TE - Energy Saver Tandem Exit Check Integrated Delayed Egress Lock as manufactured by SDC Security Door Controls.

        - 1511TE - (2X) 1200 lb (544 Kg) holding force, dual coil 650/400 mA at 12/24 VDC operation.

        - Activated by door movement or sense bar unlock delay and nuisance delay per code specification.

        - Emergency release input, Mode status outputs, Digital countdown display, Selectable voice or tone warning.

** NOTE TO SPECIFIER **  Delete code compliant operation not required.

      - Operation: NA - NFPA, UBC, IBC, IFC,. (1 or 2 sec Nuisance. 15 or 30 sec Delay)

      - Operation ND -  NFPA,, UBC, IFC, IBC, SBC. (0/1 sec Nuisance. 15 sec Fixed Delay)

      - Operation NH - NFPA,, UBC, IFC, IBC, SBC. (0/1 sec Nuisance. 30 sec Fixed Delay)

      - Operation NC - NFPA,, UBC, IFC, IBC, SBC, CBC OSPHD. (0/1 sec Nuisance. 15 sec Fixed Delay. Manual Reset)

      - Operation BC – BOCA and Chicago Code. (0 sec Nuisance. 15 sec fixed Delay. 30 sec Relock)

      - Operation BH – BOCA Code. (0/1 sec Nuisance. 30 sec fixed Delay. 30 sec Relock)

      - Operation: BD – BOCA Code. 0/1 sec Nuisance. 15 sec fixed Delay. 30 sec Relock)

** NOTE TO SPECIFIER **  Delete option not required.

      - Reset & Control

        - K – Built-in Key switch for Reset & Bypass (Std)

        - P – Push switch for Reset only

        - L – Less Key or Push switch

** NOTE TO SPECIFIER **  Finish V is standard. Delete finish not required. Plated finishes are special order.

      - Finish: V - 628 Aluminum.

      - Finish: X - Dark Bronze powder coat (313/613 equal).

      - Finish: Y - 335 Black Anodized.

      - Plated Finish: Q - 626 Dull Chrome.

      - Plated Finish: C - 605 Bright Brass. Powder coat

      - Plated Finish: D - 606 Dull Brass. Powder coat

      - Plated Finish: P - 625 Bright Chrome.

- ** NOTE TO SPECIFIER **  Delete options not required.  Options D, B, & A specify two for tandem.

      - Options: E - Energy Saver. 1200 lbs holding force, low power consumption.

      - Options: D - Door Position Status. Provides remote monitoring.

      - Options: B - Magnetic Bond Alert Sensor.

      - Options: A - Anti-tamper Switch. Detects attempt to remove the access cover.

      - Options: VI - One Language or Bilingual - Spanish, English and Spanish, English and French verbal notification.

      - Options: 101-SP - External 15 Watt Speaker.