  - ELECTRIC BOLT LOCKS

** NOTE TO SPECIFIER **  The Spacesaver®, first designed and patented by SDC, is a fundamental innovation in electric locking technology for access control applications. The stainless steel bolt projects at right angles to the lock mechanism, allowing installation of Spacesaver® locks, by means of a simple cutout, in virtually any standard 1.5 inches frame. , or in most door lock stiles. Delete if not required.

** NOTE TO SPECIFIER **  The SDC GL160 and GL260 series electromechanical GateLoks are designed to provide access control and remote locking and unlocking capability for manual or automatic chain link, tubular steel and wrought iron sliding or swinging gates.

    - Gate Lock: Gate locks shall be designed for a 3 inches (76mm) fence post and 2 inches (51mm) gate post and shall be adaptable to smaller sizes.12/24 VDC  900/450 mA.

** NOTE TO SPECIFIER **  Delete model not required.

      - Product: Model GL160AI - Failsafe gate lock, 12/24VDC.

        - Operation: The GL160A GateLok shall be unlocked by an access control and remote control. While handing is required they are field reversible.

      - Product: Model GL163AI - Failsafe gate lock, built-in keyswitch 12/24VDC.

        - Operation: The GL163A GateLok shall be unlocked by an access control, remote control and built-in keyswitch. Handing is required and they are not field reversible.

      - Product: Model GL260AH - Failsecure gate lock 12/24VDC.

        - Operation: The GL260A GateLok shall be unlocked by an access control and remote control. While handing is required they are field reversible.

        - Caution- Will not unlock with power outage.

      - Product: Model GL263AH - Failsecure gate lock, built-in keyswitch, 12/24VDC. (Mortise cylinder by others)

        - Operation: The GL263A GateLok may be unlocked by an access control, remote control and built-in key switch. The  key switch is for momentary electrical override and does not maintain a sustained unlocked mode. Handing is required and the lock is not field reversible.

        - Caution - Will not unlock during power outage.

      - Product: Model GL260MRAH - Failsecure gate lock, mechanical key release, 12/24VDC.

        - Operation: The GL260MRA GateLok may be unlocked by an access control, remote control and mechanical key release. The mechanical key is for momentary override and does not maintain a sustained unlocked mode. The mechanical key retracts the bolt even during power outage.  While handing is required they are field reversible.

      - Size:  5 inches W by 6.5 inches H by 2 inches D (127 by 16.5 by 50.8 mm)

      - Material:  0.125 (3.2 mm) steel.

      - Bolt:  0.625 inch diameter by 0.625 inch throw (15.9 mm by 15.9 mm).

      - Key Cylinder:  ANSI 1.125 inches or 1.250 inches. Standard or interchangeable core mortise key cylinder. Provided by others.

      - Adjustable Auto Relock Switch keeps the bolt retracted until the gate is in the closed position.

      - Mortise key cylinder provided by others.

** NOTE TO SPECIFIER **  Delete options not required.

      - Accessory: D - Gate position sensor SPDT, 10 Amp at 30 VDC.

      - Accessory: B - Bolt lock position sensor, 10 Amp at 30 VDC.

      - Accessory: BR64XL - Rectifier for AC operation.