  - ELECTRIFIED EXIT DEVICE (Check with factory when multiple electrified options are required for an exit bar)

    - Exit Devices:

      - Product: Spectra S6000 Series Exit Device as manufactured by SDC Security Door Controls

      - UL & ULC Listed panic and fire exit hardware. ANSI/BHMA A156.3-2001 Grade 1 Compliant. CA Title 19 Compliant. Meets/Exceeds ADA requirements. UBC 97, Standard 7.2.

** NOTE TO SPECIFIER **  Model Delete models not required.

      - Model S61 - Rim or rim mount.

      - Model S62 – Surface Vertical Rod

      - Model S63 – Mortise

      - Model S68 – Concealed Vertical Rod (Special order only. Consult SDC factory)

** NOTE TO SPECIFIER **  ANSI Functions: Delete functions not required.

      - Function: 01 - Exit only, No Trim.

      - Function: 02 - Dummy Pull or Lever (opens when dogged).

      - Function: 03 - Pull with cylinder or cylinder only, key latch retraction.

      - Function: 08 - Lever with key locks/unlocks lever.

      - Function: 14 - Lever trim always active.

** NOTE TO SPECIFIER **  Panic or Fire Rated. Delete dogging not required.

      - Dogging: P - Panic Exit Device, mechanical dogging.

      - Dogging: P CD - Panic Exit Device, key cylinder dogging. (Mortise Cyl not included)

      - Dogging: F - Fire Exit Device, dogging not permitted.

** NOTE TO SPECIFIER **  Delete handing not required.

      - Handing: RR - Right hand reverse bevel, RHRB.

      - Handing: LR - Left hand reverse bevel, LHRB.

** NOTE TO SPECIFIER **  Finish

      - Finish: U - 630 Dull Stainless Steel. (Std)

** NOTE TO SPECIFIER **  Length: Delete door width not required.

      - Length: 36 inches (914 mm) door. (Std)**

      - Length: 42 inches (1067 mm) door.

      - Length: 48 inches (1219 mm) door.

** NOTE TO SPECIFIER **  Delete signal output not required.

      - Signal Output: R - Request-To-Exit Output, SPDT.

      - Signal Output: L - Latch Status Output, SPDT.

** NOTE TO SPECIFIER **  Electrified Latch Retraction for rim mount, vertical rod and mortise. Delete remote operation if not required. For use with SDC 602RF and 632RF Power Supplies.

      - Remote Operation: E - Electric Latch Retraction.

        - Voltage: 24 VDC at 700mA activation, 200 mA continuous.

        - Operation: Momentary or maintained latch bolt and push pad retraction.

        - EMC - Sequencer Module required for pair of doors and automatic doors. 24 VDC.

** NOTE TO SPECIFIER **  Electrified Mortise Exit Devices. Delete remote operation if not required.

      - Remote Operation: M - Electrified Mortise Exit Devices. MF – Fail Safe or MS – Fail Secure

        - Field reversible failsecure/failsafe, unlocks by access control. Failsafe unlocks upon power loss or signal from fire command center. Door stays latched even when unlocked.

        - Complies with national building and fire codes.

        - 12/24 VDC at 600/300 mA.

** NOTE TO SPECIFIER **  Options: Delete if not required.

        - Provide DPS - Door Position Status.

        - Provide L – Latch status.

** NOTE TO SPECIFIER **  Electrified dogging. Delete if not required.

      - Operation: G - Electric Dogging. Exit bar pad must be manually pushed down for electric dogging to hold exit bar pad down.

        - Voltage: 12/24VDC at 170/100 mA.

** NOTE TO SPECIFIER **  Options: Delete if not required.

        - KS - Built-in on/off key switch. (Cylinder not included)

** NOTE TO SPECIFIER **  Delete if not required.

      - Controlled Access Fire Exit Device: Hitower Pro S6303FH Frame Actuator Controlled Fire Exit Device as manufactured by SDC Security Door Controls.

        - Failsafe operation and unlocks by access control, power loss or signal from fire command center. Door stays latched even when unlocked. All wiring is maintained in the strike jamb. Complies with national building and fire codes.

        - Specify handing: LHR,RHR

** NOTE TO SPECIFIER **  Delete voltage that is not required.

        - Voltage: 24 VDC, 500mA

        - Voltage: 24 VAC, 500mA

        - Voltage: 115 VAC, 500mA

** NOTE TO SPECIFIER **  Delete if not required. Not available with other options – E,G, Alarm A/B

      - Delayed Egress: Provide S6000 Model DE - Electrification of exit device and wall mount controller with keypad control of REX, Bypass and reset. 24 VDC, 430mA

** NOTE TO SPECIFIER **  Delete accessory not required.

        - Optional - Provide DEC-J - 3 Gang Interior surface mount box for          S6000 DE/KDE.

        - Optional - Provide Model S6000 DES Slave Exit bar for double doors. Exit bar equipped with Delayed Egress mechanism, less controller. Must be ordered together with S6000 DE/KDE Exit device. DES – 24VDC, 250mA.

** NOTE TO SPECIFIER **  Delete if not required. Not available with other options – E,G, Alarm A/B

      - Delayed Egress: Provide S6000 Model KDE - Electrification of exit device and wall mount controller with both keypad and key switch control for Bypass and Reset, less cylinder. 24VDC, 430mA.

Optional - Provide DEC-J Surface box and/or S6000 DES Slave Exit bar as required.

      - Delayed Egress: Provide S6000 Model 101 All-In-One Delayed Egress Exit Device. Electrification of exit device with Delayed egress electronics built into exit bar. Mortise cylinder key switch provides REX, Reset and Bypass at exit device. LED status indicator of Armed/Alarm/Bypass. 24VDC, 540mA (Mortise cylinder not included)

        - Provide Model S6000 DES Slave Exit bar for double doors. Exit bar equipped with Delayed Egress mechanism, less electronics. Must be ordered together with S6000 101 Exit device.           DES – 24VDC, 250mA.

        - Optional – Provide MC-4 Door Position Contact per door leaf

        - Optional – Provide PTM-10 Ten conductor power transfer device per door leaf.

        - Optional – Provide PTH-10DPS Ten conductor transfer hinge with Door position contact (DPS) per door leaf.

        - Optional – Provide PT-5 Concealed Power Transfer device per door leaf.

      - Delayed Egress Code suffixes for S6000 Models DE/KDE/101.

        - NC – IBC, IFC, NFPA 101, NFPA1-UFC, UBC, SBC compliant, Fixed 15 second Exit delay, 0/1 second Nuisance delay. CBC OSHPD/Manual Power up.

        - ND – IBC, IFC, NFPA 101, NFPA1-UFC, UBC, SBC compliant, fixed 15 second Exit delay, 0/1 second Nuisance delay.

        - BC – BOCA National Building Code and Chicago Building compliant. 15 second Fixed Exit delay, 0 second Nuisance delay, Auto Reset 30 seconds after door closure.

        - BD – BOCA National Building Code compliant. 15 second Fixed Exit delay, 0/1 second Nuisance delay, Auto Reset 30 seconds after door closure.

        - NA (for S6000 DE/KDE Only) – NFPA, IBC, and IFC compliant, Selectable 15/30 second Exit delay, selectable 1 or 2 second Nuisance delay. Selectable Automatic or Manual power up after emergency release.

** NOTE TO SPECIFIER **  Exit alarm kit for rim mount, mortise, vertical rod. Delete if not required. Not available with other options – E, G, DE/KDE/101

      - Exit Alarm: Model A - Exit Alarm, 9V Battery Powered.

      - Exit Alarm: Model B - Exit Alarm with 12/24V AC/DC input (9V battery provides power backup).

** NOTE TO SPECIFIER **  Alarm Options. Delete alarm not required.

        - AR6 - 6 or 10 minute alarm with auto rearm and manual key reset.

        - AR20 - 20 minute alarm with auto rearm and manual key reset.

        - AD1 - 1 second arming delay.

** NOTE TO SPECIFIER **  Trim: Delete trim not required.

      - Mechanical Trim: EK - Eclipse (Function and finish to match device).

      - Mechanical Trim: GK - Galaxy (Function and finish to match device).

      - Mechanical Trim: SP - Saturn (Function and finish to match device).

** NOTE TO SPECIFIER **  Electric Trim: Delete trim not required.

      - Electrified Trim: EKE03 - Eclipse (finish to match device).

      - Electrified Trim: EKE03_LT - Eclipse with LED (finish to match device).

      - Electrified Trim: GKE03 - Galaxy (finish to match device).

      - Electrified Trim: GKE03_LT -  Galaxy with LED (finish to match device).

        - Failsecure, field reversible to failsafe, audible tone, 4 ft cable and connectors, 12/24 VDC at 600/300 mA.

** NOTE TO SPECIFIER **  Delete Electric Trim Options not required.

        - LT - Tricolor LED Indicator.

        - LS - Locked/unlocked status, SPDT 3 Amp contact.